## Correct Refrigerant Charge

### Description

This energy efficiency measure (EEM) applies a performance degradation factor to all existing DX heating and cooling coils in a model, representing the estimated impact of a 30% refrigerant undercharge scenario. An estimated degradation in performance equal to a (11.1% / 2.77%) reduction of the DX (cooling / heating) coil’s current rated COP is applied. This value represents an estimated coil performance degradation associated with a 30% refrigerant undercharge scenario. The value for the degradation factor is based on research work recently performed by NIST in collaboration with ACCA and published under IEA Annex 36 in 2015.

### Modeler Description

This energy efficiency measure (EEM) loops through all DX Coil objects of these types:                                  1) OS:CoilCoolingDXMultiSpeed, 2) OS:CoilCoolingDXSingleSpeed, 3) OS:CoilCoolingDXTwoSpeed, 4) OS:CoilCoolingDXTwoStageWithHumidityControlMode, 5) OS:CoilCoolingDXSingleSpeed, 6) OS:CoilCoolingWaterToAirHeatPump:EquationFit and 7) OS:CoilCoolingWaterToAirHeatPump:EquationFit. For each DX Cooling Coil object type, the initial Rated COP is modified (reduced) by 11.1%, representing a 30% refrigerant undercharge scenario. For each DX Heating Coil object type, the initial Rated COP is modified (reduced) by 8.24%, representing a 30% refrigerant undercharge scenario.

### Use Case Types

Retrofit EE

### Arguments

No arguments

### Initial Condition Message

The initial model contained {X} applicable DX Heating coil objects for which this measure is applicable.

The initial model contained {Y} applicable DX Cooling coil objects for which this measure is applicable.

### Final Condition Message

{A} DX Heating Coil objects were modified to incorporate estimated performance degradation for a 30% (by mass) refrigerant undercharge scenario.

{B} DX Cooling Coil objects were modified to incorporate estimated performance degradation for a 30% (by mass) refrigerant undercharge scenario.

### Not Applicable Messages

The model contains no DX Heating or DX Cooling coil objects for which this measure is applicable.

### Warning Messages

None

### Information Messages

Did something to object 1. Etc.

### Error Messages

### None

### Code Outline

Loop through each type of object described below to find these objects. Modify the Rated COP by (1-0.111)

If object type = OS:CoilCoolingDXMultiSpeed

- Read OS:CoilCoolingDXMultiSpeed .stages (maximum number of stages)

  - For each stage, read OS:CoilCoolingDXMultiSpeedStageData

    - OS:CoilCoolingDXMultiSpeedStageData.grossRatedCoolingCOP = OS:CoilCoolingDXMultiSpeedStageData.grossRatedCoolingCOP * (1-0.111)

If object type = OS:CoilCoolingDXSingleSpeed

- OS:CoilCoolingDXSingleSpeed.ratedCOP = OS:CoilCoolingDXSingleSpeed.ratedCOP * (1-0.111)

If object type = OS:CoilCoolingDXTwoSpeed

- OS:CoilCoolingDXTwoSpeed.ratedHighSpeedCOP = OS:CoilCoolingDXTwoSpeed.ratedHighSpeedCOP *  (1-0.111)

- OS:CoilCoolingDXTwoSpeed.ratedLowSpeedCOP = OS:CoilCoolingDXTwoSpeed.ratedLowSpeedCOP *  (1-0.111)

If object type = OS:CoilCoolingDXTwoStageWithHumidityControlMode

- OS:CoilCoolingDXTwoStageWithHumidityControlMode.normalModeStage1CoilPerformance.grossRatedCOP = OS:CoilCoolingDXTwoStageWithHumidityControlMode.normalModeStage1CoilPerformance.grossRatedCOP *  (1-0.111)

- OS:CoilCoolingDXTwoStageWithHumidityControlMode.normalModeStage1Plus2CoilPerformance.grossRatedCOP = OS:CoilCoolingDXTwoStageWithHumidityControlMode.normalModeStage1Plus2CoilPerformance.grossRatedCOP *  (1-0.111)

- OS:CoilCoolingDXTwoStageWithHumidityControlMode.dehumidificationMode1Stage1CoilPerformance.grossRatedCOP = OS:CoilCoolingDXTwoStageWithHumidityControlMode.dehumidificationMode1Stage1CoilPerformance.grossRatedCOP *  (1-0.111)

- OS:CoilCoolingDXTwoStageWithHumidityControlMode.dehumidificationMode1Stage1Plus2CoilPerformance.grossRatedCOP = OS:CoilCoolingDXTwoStageWithHumidityControlMode.dehumidificationMode1Stage1Plus2CoilPerformance.grossRatedCOP *  (1-0.111)

If object type = OS:CoilHeatingDXSingleSpeed

- OS:CoilHeatingDXSingleSpeed.ratedCOP = OS:CoilHeatingDXSingleSpeed.ratedCOP * (1-0.0277)

### Tests

This measure applies to:

- Secondary School

- Primary School

- Outpatient Healthcare

- Large Office

- Warehouse

- Midrise Apartment

- Small Office

- Medium Office

- Stand-Alone Retail

- Strip Mall

- Supermarket

- Quick Service Restaurant

- Full Service Restaurant

- Small Hotel

This measure does not apply to:

- Hospital

- Large Hotel

Test results:

Run the simulation using prototype .osm files, examine the results, cut and paste some before/after screenshots/evidence that makes you think that the measure is working correctly, including generating messages.

Engineering Notes:

The coil performance degradation factors calculated to represent a 30% refrigerant undercharge scenario were determined by recently published research conducted by NIST/IEA under IEA Annex 36: Quality Installation/Quality Maintenance Sensitivity Analysis

“Effect of Installation Faults on Air-to-Air Heat Pump Performance”:

http://www.nist.gov/manuscript-publication-search.cfm?pub_id=917726

“NIST Technical Note 1848: Sensitivity Analysis of Installation Faults on Heat Pump Performance”: http://nvlpubs.nist.gov/nistpubs/TechnicalNotes/NIST.TN.1848.pdf

“Normalized Performance Parameters for a Residential Heat Pump in the Cooling Mode with Single Faults Imposed”: http://www.nist.gov/customcf/get_pdf.cfm?pub_id=910617

The published research recommends an upper fault limit of 30% undercharge (where % = % mass below the correct (no fault) charge).  A spreadsheet implementation of the published heat pump performance degradation correlations (single fault approach) using national average outdoor conditions and seasonal indoor temperatures of 72F was used to generate the following results:

30% refrigerant undercharge = 11.10% reduction from nameplate Cooling COP

30% refrigerant undercharge = 2.77% reduction from nameplate Heating COP

For Reference:

20% refrigerant undercharge = 6.90% reduction from nameplate Cooling COP

20% refrigerant undercharge = ~0.00.% reduction from nameplate Heating COP

10% refrigerant undercharge = 3.33% reduction from nameplate Cooling COP

10% refrigerant undercharge = ~ 0% reduction from nameplate Heating COP