## Sheet1
ID | Measure | Brief Description
Re-tuning Measures
1 | Sensor calibration (sensor faults) | Correct the sensor offsets for economizer control. Three severity levels (i.e., offset of 1, 3 and 5 °C) are considered for both the outdoor-air temperature sensor and the mixed-air temperature sensor.
2 | Correct refrigerant charge | Restore the refrigerant charge to the recommended level for roof top units. Three severity levels are considered: undercharge by 10%, 20%, and 30%.
3 | Fix water coil valve leakages | Fix heating/cooling coil valve leakages to avoid simultaneous heating and cooling. Heating coil leakage with three severity levels are considered in this work.
4 | Correct HVAC operation schedules | Correct (shorten) the scheduled HVAC operations hours to closely match the occupancy schedule. Two severity levels are considered: HVAC running 2 hours and 4 hours longer than needed every day from Monday to Saturday.
5 | Supply air temperature setpoint reset | Reset AHU's supply air temperature based on a seasonal schedule or outside air temperature.
6 | Reduce economizer damper leakage | Add blade and jamb seals to reduce damper leakages.
7 | Exhaust fan shut down during unoccupied periods | Exhaust fans interlock with air-handling units and do not run continuously.
8 | Static pressure reset | Reduce the supply fan static pressure when the zone thermal loads are decreased. This measure was modeled with two different control strategies: 1) halve the supply-fan pressure after 5:00 pm (off office hours) via a schedule; and 2) reset the supply-fan pressure based on the damper positions of terminal units.
9 | Close outdoor air damper during unoccupied periods | Close the outside air damper during the early morning warm-up and cool-down periods before normal occupancy.
10 | Plant shut down when there is no load | Operate the central plant (chillers, boilers, tower fans, pumps) based on heating or cooling demand from the coils and the outdoor air temperature, instead of continuous running.
11 | Chilled water pump differential pressure reset | Reset chilled water loop's differential pressure based on load conditions.
12 | Chilled water supply temperature reset | Raise the chilled water supply temperature setpoint during periods of low cooling load. This measure was modeled with two different control strategies: 1) reset the chilled water supply temperature according to a seasonal schedule; and 2) reset the temperature based on cooling coil load conditions.
13 | Condenser water temperature reset | Reset the tower outlet temperature based on outdoor air conditions.
14 | Hot water pump differential pressure reset | Reset hot water pump loop's differential pressure based on load conditions.
15 | Hot water supply temperature reset | Reduce the hot water supply temperature setpoint during periods of low heating load (e.g., in warm weather conditions).
16 | Lower minimum air flow rate for VAV terminals | Reduce the minimum air flow to 25% of the maximum for all VAV boxes except those serving the conference rooms.
17 | Widen thermostat setpoint deadband (including nonoccupied period) | Space temperature set points are widened to have at least 5°F difference between heating and cooling set points during the occupied period. Reset heating and cooling set points to 60°F and 80°F during unoccupied periods.
Advanced Control Measures
18 | Demand-controlled ventilation | Control the amount of outdoor air based on space ventilation needs using a proxy CO2 sensor.
19 | Occupancy sensor for lighting control | Use occupancy sensors to control general lighting in the following spaces: open offices, private offices, conference rooms, restrooms, stairways, and break rooms.
20 | Daylight control | Dim overhead lighting fixtures continuously to maintain the desired illuminance set point at 300 lux for perimeter zones.
21 | Exterior lighting control | Lower parking lights to 25% of the full power at 7 p.m. and remain at that level for the rest of the night.
22 | Advanced on/off control for plug loads | Turn off plug loads when they are not in use (smart power strips for task lighting and office equipment, vendingmiser for vending machines, time switches for water coolers).
23 | Night purge ventilation | Cool the building at night using 100% outside when appropriate.
24 | Advanced RTU Controls | Add a VFD to existing RTUs and apply different fan speeds according to the RTU operation mode.
25 | Control elevator cab lighting and ventilation control | Use motion sensor in elevator cabs to turn off lights and ventilation when the cabs are unoccupied.
26 | Water-side economizer | Add or activate the water-side economizer to use cooled water from the cooling tower to indirectly cool the indoor space.
27 | Cooling tower controls (variable-speed fan) | Add VFD to the cooling towers and activate as many cells as possible down to 20% fan speed or other possible values.
Predictive and Optimal Control Measures
28 | Plant optimization | Minimize kW/ton for the whole chiller plant through the control of chiller sequencing, leaving chilled water temperature, tower outlet temperature, and chilled water pump differential pressure.
29 | VAV system optimization | Minimize the air system energy through the control of discharge air temperature and supply fan static pressure based on zone load conditions.
30 | VAV dynamic ventilation control | Reset the VAV system ventilation rate dynamically based on the system flow rate and the terminal damper positions
31 | Whole building optimization | Optimize building operation considering the interactions among different HVAC equipment, HVAC and lighting, weather conditions.
32 | Predictive controls | Change HVAC system control strategies based on the predicted load and weather conditions.
33 | Optimal start/stop | Start and stop HVAC equipment based on indoor and outdoor temperatures instead of a fixed schedule.
Grid Demand Response (DR) Measures
34 | Setpoint changes for demand response (DR) | Reset thermostat setpoints for demand response.
35 | Duty cycle for DR | Alternate HVAC equipment operations for power demand limiting.
36 | Pre-cooling for DR | Pre-cool spaces for shifting electricity demand.
37 | Lighting controls for DR | Reduce lighting energy for demand response.
38 | Chilled water temperature control with fan controls | Maintain supply fan speed while raising the supply chilled water temperature setpoint.
39 | Thermal energy storage | Use chilled water or ice storage for load management.
40 | Ancillary services | Curtail electric power use whenever the grid needs.
Retrofit Measures
41 | Interior lighting retrofit to reduce LPD | Replace interior lighting fixtures with higher-efficiency ones and improve lighting design.
42 | Exterior lighting fixtures retrofit | Replace exterior lighting fixtures with higher-efficiency ones.
43 | Replace supply fan motor and VFD (for variable-speed fans) | Replace supply fan motors and VFDs with premium efficiency motors and VFDs with current technology.
44 | Replace boilers with higher efficiency models | Replace existing boilers with newer models that have higher heating efficiency.
45 | Replace chillers with higher efficiency models | Replace existing chillers with newer models that have higher cooling efficiency.
46 | Replace RTUs with higher efficiency units | Replace existing RTUs with newer models that have higher cooling and heating efficiency.
47 | Replace RTUs with units that use evaporative cooling | Replace air-cooled air conditioners with evaporatively cooled conditioners in hot and dry climates.
48 | Replace RTUs with air-to-air heat pumps | Replace RTUs with gas heat wtih air-to-air heat pumps in mild climates.
49 | Increase efficiency of service hot water systems | Replace the water heater with a more efficient model.
50 | Retrofit electric transformers with higher efficiency models | Upgrade the low-voltage distribution transformers, for which the transformer loss is usually included in building utility cost, to higher efficiency models.
51 | Replace windows | Replace old, inefficient window assemblies with newer ones having better thermal performance. Two levels were considered: ASHRAE STD 90.1-2010 minimum requirement and AEDG-50% recommendations.
52 | Add wall insulation | Add additional insulation to existing walls to reduce the amount of heat transfer. Two levels were considered: ASHRAE STD 90.1-2010 minimum requirement and AEDG-50% recommendations.
53 | Add roof insulation | Add additional insulation to the roof to reduce the amount of heat transfer. Two levels were considered: ASHRAE STD 90.1-2010 minimum requirement and AEDG-50% recommendations.